JSC Mozyr OR

Passport No 1090

Fuel oil 100

3,0 % ashy with setting temperature 25 ºC

GOST 10585-2013

Lot number: 1090

Production date 01.08.2018          Tank № 12                           Innage  983 sm

| No | Parameters | Units | Testing method | GOST 10585-2013 | Factual |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Limit min | Limit max |  |
| 1 | Kinematic viscosity at 100 ºC | mm²/s | STB ISO 3104 |  | 50,00 | 47,08 |
| 2 | Ash content, for fuel oil: low-ashy ashy | % | GOST 1461 | - - | 0,05 0,14 | 0,10 |
| 3 | Mass fraction of mechanical impurities | % | GOST 6370 | - | 1,0 | 0,08 |
| 4 | Water mass fraction | % | GOST 2477 | - | 1,0 | 0,1 |
| 5 | Content of water-soluble acids and alkalies | - | GOST 6307, p.7.5 GOST 10585 | None | None |
| 6 | Sulfur mass fraction * | % | STB 1420 |  | 0,5 1,0 1,5 2,0 2,5 3,0 3,5 | 2,51 |
| 7 | Content of H2S | ppm (mg/kg) | GOST P 53716 | - | 10** | 9,5 |
| 8 | Open-cup flash-point *** | ºC | GOST 4333 | 110 | - | 144 |
| 9 | Setting point | ºC | GOST 20287 (method B) | - | 25 | 12 |
| 10 | Combustion value (min) as converted for dry fuel (non-sorting), for fuel oil wish content of sulphur, %: 0.50, 1.00, 1.50, 2.00 2.50, 3.00, 3.50 | kJ/kg | STB 1663 (ASTM D 240) | 40530 39900 |  | 39900 |
| 11 | Density at 15 ºC | kg/m³ | GOST 31072 | No rated Estimation is mandatory | 1016,6 |
| 12 | Fractional yield under 350°C | % vol. | ASTM D 1160 | - | 17** | 13,3 |

*standart of Technical Regulation of Customs Union 013/2011 – max 3,5 %

** standart, established  in territory of Russian Federation

*** standart of Technical Regulation of Customs Union 013/2011 – min 90 ºC

Information about additive: no additives.

Information about declaration of conformity: № TC  BY/112 11.01. TP013 002 03761, valid  until 28.03.2019

Conclusion: the standard product corresponds to GOST 10585-2013 requirements and Technical Regulation of Customs Union 013/2011.

Additionally for customs clearing in supply of exports:

Initial boiling point, ºC, STB 1934 (ASTM D 86) – 240,1

Distilled to 250 ºC, % vol., STB 1934 (ASTM D 86) – 0,4

Quantity of kerosine-gasoil fractions, stilled till 350 ºC, % vol., STB 1559 (ASTM D 1160) – 13,3

Open-cup flash-point, ºC, STB 1651 (ASTM D 92) – 144

Closed-cup flash-point, ºC, STB ISO 2719 – 104

Kinematic viscosity at 50 ºC,  mm2/s, STB ISO 3104 (ISO 3104) – 729,7

Colorimetric characteristic, ASTM D 1500 – min 8

For information: density at 20 ºC, kg/m³ - 1011,8